## Lux Calculation
LUX CALCULATION
FLOOR | S.N. | TYPES OF SPACE | AREA (mm^2) | REQUIRED LUX | BULB WATTAGE(W) | BULB EFFICIENCY | BULB LUMEN | µm | µu | N0. OF LUMINARIES
GROUND FLOOR PLAN | 1 | Foyer | 22.15 | 150 | 20 | 100 | 2000 | 0.8 | 0.8 | 2.5957
| 2 | Foyer | 50 | 150 | 20 | 100 | 2000 | 0.8 | 0.8 | 5.8594
| 3 | Cash Counter | 11.1 | 200 | 20 | 100 | 2000 | 0.8 | 0.8 | 1.7344
| 4 | Emergency Ward | 54 | 200 | 36 | 100 | 3600 | 0.8 | 0.8 | 4.6875
| 5 | Nurse Station | 7.1 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.4792
| 6 | Nurse Room | 6.2 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.2917
| 7 | Foyer | 12.71 | 150 | 40 | 100 | 4000 | 0.8 | 0.8 | 0.74473
| 8 | Doctor's Room | 10.98 | 250 | 36 | 100 | 3600 | 0.8 | 0.8 | 1.1914
| 9 | Isolated Observation | 8.8 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.8333
| 10 | Back Office | 6.15 | 200 | 20 | 100 | 2000 | 0.8 | 0.8 | 0.96094
| 11 | Front Desk | 9.12 | 200 | 20 | 100 | 2000 | 0.8 | 0.8 | 1.425
| 12 | Minor OT ** | 21.89 | 200 | 36 | 100 | 3600 | 0.8 | 0.8 | 1.9002
| 13 | Sample Collection | 11.62 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 2.4208
| 14 | Pathology Lab | 16.47 | 150 | 100 | 100 | 10000 | 0.8 | 0.8 | 0.38602
| 15 | Delivery Room | 29.61 | 250 | 15 | 100 | 1500 | 0.8 | 0.8 | 7.7109
| 16 | Clean Utility Room | 8.7 | 300 | 15 | 100 | 1500 | 0.8 | 0.8 | 2.7188
| 17 | Neonatal Stabalization | 17.37 | 150 | 15 | 100 | 1500 | 0.8 | 0.8 | 2.7141
| 18 | Nurse Room | 5.3 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.1042
| 19 | Nurse Station | 5.3 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.1042
| 20 | Doctor's Room | 8.16 | 250 | 20 | 100 | 2000 | 0.8 | 0.8 | 1.5938
| 21 | Waiting Area | 35.414 | 150 | 40 | 100 | 4000 | 0.8 | 0.8 | 2.075
| 22 | DOTS Clinic | 22.14 | 250 | 36 | 100 | 3600 | 0.8 | 0.8 | 2.4023
| 23 | Back Office | 12.86 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 2.6792
| 24 | Front Desk | 9.39 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.9563
| 25 | Foyer | 36.584 | 150 | 40 | 100 | 4000 | 0.8 | 0.8 | 2.1436
| 26 | Pharmacy | 11.28 | 250 | 36 | 100 | 3600 | 0.8 | 0.8 | 1.224
| 27 | Store | 5.87 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.2229
| 28 | Control Room | 6.3 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.3125
| 29 | X-Ray Room | 18.18 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 3.7875
| 30 | Labour Room | 29.81 | 150 | 15 | 100 | 1500 | 0.8 | 0.8 | 4.6578
| 31 | Scrub Area | 3.57 | 200 | 6 | 100 | 600 | 0.8 | 0.8 | 1.8594
| 32 | Operation Theatre | 42.9 | 200 | 36 | 100 | 3600 | 0.8 | 0.8 | 3.724
| 33 | Sluice | 5.87 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.2229
| 34 | Clean Utility Room | 5.9 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.2292
FIRST FLOOR PLAN | 35 | Foyer | 33.7 | 150 | 40 | 100 | 4000 | 0.8 | 0.8 | 1.9746
| 36 | Foyer | 70.46 | 150 | 40 | 100 | 4000 | 0.8 | 0.8 | 4.1285
| 37 | Doctor's Room | 7.36 | 200 | 20 | 100 | 2000 | 0.8 | 0.8 | 1.15
| 38 | Nurse Station | 10.89 | 150 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.7016
| 39 | Foot Operative 3 bed | 35.18 | 250 | 36 | 100 | 3600 | 0.8 | 0.8 | 3.8173
| 40 | General Ward 8 bed | 77.4 | 200 | 36 | 100 | 3600 | 0.8 | 0.8 | 6.7188
| 41 | Single Cabin | 9.62 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 2.0042
| 42 | Nurse Room | 17.04 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 3.55
| 43 | Observation Room | 36.74 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 7.6542
| 44 | Nurse Station | 16.58 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 3.4542
| 45 | Foyer | 63.19 | 150 | 40 | 100 | 4000 | 0.8 | 0.8 | 3.7025
| 46 | General Clinic | 22.12 | 250 | 36 | 100 | 3600 | 0.8 | 0.8 | 2.4002
| 47 | Treatment/ Dressing Room | 22.12 | 250 | 36 | 100 | 3600 | 0.8 | 0.8 | 2.4002
| 48 | Fp Consultant | 37.35 | 200 | 36 | 100 | 3600 | 0.8 | 0.8 | 3.2422
| 49 | Echo TMT Ultrasound Room | 27.28 | 250 | 20 | 100 | 2000 | 0.8 | 0.8 | 5.3281
| 50 | Dental Clinic | 29.75 | 250 | 36 | 100 | 3600 | 0.8 | 0.8 | 3.2281
| 51 | Discussion Area | 15.36 | 200 | 20 | 100 | 2000 | 0.8 | 0.8 | 2.4
| 52 | Preparation Area | 15.121 | 200 | 20 | 100 | 2000 | 0.8 | 0.8 | 2.3627
| 53 | Sluice | 5.87 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.2229
| 54 | Operation Theatre | 36.5 | 200 | 36 | 100 | 3600 | 0.8 | 0.8 | 3.1684
| 55 | Store | 10.73 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 2.2354
| 56 | Chemical Store | 5.78 | 250 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.5052
SECOND FLOOR PLAN | 57 | Foyer | 33.7 | 150 | 40 | 100 | 4000 | 0.8 | 0.8 | 1.9746
| 58 | Foyer | 70.46 | 150 | 40 | 100 | 4000 | 0.8 | 0.8 | 4.1285
| 59 | Doctor's Room | 7.36 | 200 | 20 | 100 | 2000 | 0.8 | 0.8 | 1.15
| 60 | Nurse Station | 10.89 | 150 | 15 | 100 | 1500 | 0.8 | 0.8 | 1.7016
| 61 | Foot Operative 3 bed | 35.18 | 250 | 36 | 100 | 3600 | 0.8 | 0.8 | 3.8173
| 62 | General Ward 8 bed | 77.4 | 200 | 36 | 100 | 3600 | 0.8 | 0.8 | 6.7188
| 63 | Single Cabin | 9.62 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 2.0042
| 64 | Washing Area | 39.5 | 150 | 15 | 100 | 1500 | 0.8 | 0.8 | 6.1719
| 65 | Store and Drying | 14.96 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 3.1167
| 66 | Issue Packing Ironing | 29.86 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 6.2208
| 67 | Store/Mechanical Room | 25.5 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 5.3125
| 68 | Autoclave | 17.14 | 200 | 15 | 100 | 1500 | 0.8 | 0.8 | 3.5708

## Load Calculation
HOSPITAL LOAD CALCULATION
| Hospital DBs | Electrical Loads |  |  |  | Apparent Power, kVA | Ku | Apparent Power Demand,kVA | Ks | Apparent Power Demand,kVA | Ks | Apparent Power Demand, kVA | Apparent Power Demand, kVA | Ks | Total Apparent Power Demand kVA | Size of Main MCCB of hospital, A | Total Size of sub MCCB, A | Size of Floor DBs MCCB,A
|  |  | Qty | Wattage, W | P.F
SDB 0 | SDB 0-1 | LED Panel Surface type 2x2 | 5 | 36 | 0.9 | 0.2 | 1 | 0.2 | 1 | 0.2 | 1 | 3.9443 | 58.6256 | 0.97 | 129.4768 | 187.6475 | 14.8468 | 84.9646
|  | LED Panel Surface type 1x4 | 4 | 40 | 0.9 | 0.17778 | 1 | 0.17778 | 1 | 0.17778
|  | LED Panel Surface type 1x1 | 12 | 15 | 0.9 | 0.2 | 1 | 0.2 | 1 | 0.2
|  | LED Panel Surface type 1x2 | 4 | 20 | 0.9 | 0.088889 | 1 | 0.088889 | 1 | 0.088889
|  | LED Panel Surface type 1x1 | 6 | 6 | 0.9 | 0.04 | 1 | 0.04 | 1 | 0.04 | [8 empty] | 28.9278
|  | Single Phase Socket Outlet 15 A | 2 | 1000 | 0.85 | 2.3529 | 0.97 | 2.2824 | 0.8 | 1.8259
|  | Single Phase Socket Outlet 5 A | 5 | 1000 | 0.85 | 5.8824 | 0.8 | 4.7059 | 0.3 | 1.4118
|  | Three Phase Socket Outlet | 1 | 9000 | 0.85 | 10.5882 | 0.85 | 9 | 0.7 | 6.3 | 1 | 6.3
|  | Electric Lift | 1 | 4000 | 0.8 | 5 | 0.9 | 4.5 | 1 | 4.5 | 1 | 4.5
| SDB 0-1 UPS | LED Round Emergency | 11 | 15 | 0.9 | 0.18333 | 1 | 0.18333 | 1 | 0.18333 | 1 | 6.9598 |  |  |  |  | 10.0867
|  | Single Phase Essential Socket | 16 | 1000 | 0.85 | 18.8235 | 0.9 | 16.9412 | 0.4 | 6.7765 | 1
| SDB 0-2 | LED Panel Surface type 2x2 | 4 | 36 | 0.9 | 0.16 | 1 | 0.16 | 1 | 0.16 | 1 | 7.3363 |  |  |  |  | 19.7627
|  | LED Panel Surface type 1x1 | 25 | 15 | 0.9 | 0.41667 | 1 | 0.41667 | 1 | 0.41667
|  | LED Panel Surface type 1x2 | 3 | 20 | 0.9 | 0.066667 | 1 | 0.066667 | 1 | 0.066667
|  | LED Panel Surface type 1x1 | 9 | 6 | 0.9 | 0.06 | 1 | 0.06 | 1 | 0.06
|  | Single Phase Socket Outlet | 12 | 1000 | 0.85 | 14.1176 | 0.97 | 13.6941 | 0.45 | 6.1624
|  | Single Phase Socket Outlet 5 A | 1 | 1000 | 0.85 | 1.1765 | 0.8 | 0.94118 | 0.5 | 0.47059 | [9 empty] | KVA of INVERTER
|  | Three Phase Socket Outlet | 1 | 9000 | 0.85 | 10.5882 | 0.85 | 9 | 0.7 | 6.3 | 1 | 6.3 | [7 empty] | 19.9602
| SDB 0-2 UPS | LED Round Emergency | 4 | 15 | 0.9 | 0.066667 | 1 | 0.066667 | 1 | 0.066667 |  | 5.5776 |  |  |  |  | 8.0835 |  |  | 19.2653
|  | LED Round Emergency Wall | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333 | [9 empty] | 8.4331
|  | Single Phase Essential Socket | 12 | 1000 | 0.85 | 14.1176 | 0.97 | 13.6941 | 0.4 | 5.4776 | 1
| SDB 0-3 | LED Panel Surface type 2x2 | 11 | 36 | 0.9 | 0.44 | 1 | 0.44 | 1 | 0.44 | 1 | 10.2848 |  |  |  |  | 14.9055
|  | LED Panel Surface type 1x1 | 7 | 15 | 0.9 | 0.11667 | 1 | 0.11667 | 1 | 0.11667
|  | LED Panel Surface type 1x2 | 19 | 20 | 0.9 | 0.42222 | 1 | 0.42222 | 1 | 0.42222
|  | LED Panel Surface type 1x1 | 15 | 6 | 0.9 | 0.1 | 1 | 0.1 | 1 | 0.1
|  | 48'' Celing Fan | 2 | 50 | 0.85 | 0.11765 | 0.85 | 0.1 | 1 | 0.1
|  | Single Phase Socket Outlet | 12 | 1000 | 0.85 | 14.1176 | 0.97 | 13.6941 | 0.5 | 6.8471
|  | Single Phase Socket Outlet 5 A | 8 | 1000 | 0.85 | 9.4118 | 0.8 | 7.5294 | 0.3 | 2.2588
| SDB 0-3 UPS | LED Round Emergency | 14 | 15 | 0.9 | 0.23333 | 1 | 0.23333 | 1 | 0.23333 | 1 | 7.4227 |  |  |  |  | 10.7576
|  | LED Round Emergency Wall | 3 | 15 | 0.9 | 0.05 | 1 | 0.05 | 1 | 0.05 | 1
|  | Single Phase Essential Socket | 18 | 1000 | 0.85 | 21.1765 | 0.97 | 20.5412 | 0.35 | 7.1894 | 1
SDB 1 | SDB 1-1 | LED Panel Surface type 2x2 | 10 | 36 | 0.9 | 0.4 | 1 | 0.4 | 1 | 0.4 | 1 | 8.2278 | 49.5456 |  |  |  | 11.9243 | 71.8052
|  | LED Panel Surface type 1x4 | 4 | 40 | 0.9 | 0.17778 | 1 | 0.17778 | 1 | 0.17778
|  | LED Panel Surface type 1x2 | 9 | 20 | 0.9 | 0.2 | 1 | 0.2 | 1 | 0.2
|  | LED Panel Surface type 1x1 | 6 | 6 | 0.9 | 0.04 | 1 | 0.04 | 1 | 0.04
|  | 48'' Celing Fan | 1 | 50 | 0.85 | 0.058824 | 0.85 | 0.05 | 1 | 0.05
|  | Single Phase Socket Outlet | 8 | 1000 | 0.85 | 9.4118 | 0.97 | 9.1294 | 0.6 | 5.4776 | [9 empty] | 47.6586
|  | Single Phase Socket Outlet 5 A | 5 | 1000 | 0.85 | 5.8824 | 0.8 | 4.7059 | 0.4 | 1.8824
| SDB 1-1 UPS | LED Round Emergency | 12 | 15 | 0.9 | 0.2 | 1 | 0.2 | 1 | 0.2 | 1 | 3.8518 |  |  |  |  | 5.5823
|  | Single Phase Essential Socket | 8 | 1000 | 0.85 | 9.4118 | 0.97 | 9.1294 | 0.4 | 3.6518 | 1
| SDB 1-2 | LED Panel Surface type 2x2 | 9 | 36 | 0.9 | 0.36 | 1 | 0.36 | 1 | 0.36 | 1 | 6.2986 |  |  |  |  | 29.3218
|  | LED Panel Surface type 1x4 | 6 | 40 | 0.9 | 0.26667 | 1 | 0.26667 | 1 | 0.26667
|  | LED Panel Surface type 1x1 | 17 | 15 | 0.9 | 0.28333 | 1 | 0.28333 | 1 | 0.28333
|  | LED Panel Surface type 1x2 | 6 | 20 | 0.9 | 0.13333 | 1 | 0.13333 | 1 | 0.13333
|  | LED Panel Surface type 1x1 | 3 | 6 | 0.9 | 0.02 | 1 | 0.02 | 1 | 0.02
|  | 48'' Celing Fan | 2 | 50 | 0.85 | 0.11765 | 0.85 | 0.1 | 1 | 0.1
|  | Single Phase Socket Outlet | 9 | 1000 | 0.85 | 10.5882 | 0.97 | 10.2706 | 0.5 | 5.1353
|  | Three Phase Socket Outlet | 1 | 9000 | 0.85 | 10.5882 | 0.97 | 10.2706 | 0.7 | 7.1894 | 1 | 7.1894
| SDB 1-2 UPS | LED Round Emergency | 8 | 15 | 0.9 | 0.13333 | 1 | 0.13333 | 1 | 0.13333 | 1 | 6.9804 |  |  |  |  | 10.0867
|  | Single Phase Essential Socket | 15 | 1000 | 0.85 | 17.6471 | 0.97 | 17.1176 | 0.4 | 6.8471 | 1
| SDB 1-3 | LED Panel Surface type 2x2 | 12 | 36 | 0.9 | 0.48 | 1 | 0.48 | 1 | 0.48 | 1 | 8.5644 |  |  |  |  | 12.4122 |  | 27.8909
|  | LED Panel Surface type 1x4 | 6 | 40 | 0.9 | 0.26667 | 1 | 0.26667 | 1 | 0.26667
|  | LED Panel Surface type 1x1 | 7 | 15 | 0.9 | 0.11667 | 1 | 0.11667 | 1 | 0.11667
|  | LED Panel Surface type 1x2 | 5 | 20 | 0.9 | 0.11111 | 1 | 0.11111 | 1 | 0.11111
|  | LED Panel Surface type 1x1 | 12 | 6 | 0.9 | 0.08 | 1 | 0.08 | 1 | 0.08
|  | 48'' Celing Fan | 3 | 50 | 0.85 | 0.17647 | 0.85 | 0.15 | 1 | 0.15
|  | Single Phase Socket Outlet | 8 | 1000 | 0.85 | 9.4118 | 0.97 | 9.1294 | 0.6 | 5.4776
|  | Single Phase Socket Outlet 5 A | 5 | 1000 | 0.85 | 5.8824 | 0.8 | 4.7059 | 0.4 | 1.8824
| SDB 1-3 UPS | LED Round Emergency | 11 | 15 | 0.9 | 0.18333 | 1 | 0.18333 | 1 | 0.18333 | 1 | 8.4331 |  |  |  |  | 12.2219
|  | LED Round Emergency Wall | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333 | 1
|  | Single Phase Essential Socket | 18 | 1000 | 0.85 | 21.1765 | 0.97 | 20.5412 | 0.4 | 8.2165 | 1
SDB 2 | SDB 2-1 | LED Panel Surface type 1x1 | 25 | 15 | 0.9 | 0.41667 | 1 | 0.41667 | 1 | 0.41667 | 1 | 9.0088 | 25.3101 |  |  |  | 13.0563 | 36.6813
|  | LED Round Emergency | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333
|  | Single Phase Socket Outlet | 15 | 1000 | 0.85 | 17.6471 | 0.97 | 17.1176 | 0.5 | 8.5588
| SDB 2-2 | LED Panel Surface type 2x2 | 12 | 36 | 0.9 | 0.48 | 1 | 0.48 | 1 | 0.48 | 1 | 7.8682 |  |  |  |  | 11.4031
|  | LED Panel Surface type 1x4 | 6 | 40 | 0.9 | 0.26667 | 1 | 0.26667 | 1 | 0.26667
|  | LED Panel Surface type 1x1 | 7 | 15 | 0.9 | 0.11667 | 1 | 0.11667 | 1 | 0.11667
|  | LED Panel Surface type 1x2 | 5 | 20 | 0.9 | 0.11111 | 1 | 0.11111 | 1 | 0.11111
|  | LED Panel Surface type 1x1 | 12 | 6 | 0.9 | 0.08 | 1 | 0.08 | 1 | 0.08
|  | LED Round Emergency | 11 | 15 | 0.9 | 0.18333 | 1 | 0.18333 | 1 | 0.18333
|  | LED Round Emergency Wall | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333
|  | 48'' Celing Fan | 3 | 50 | 0.85 | 0.17647 | 0.85 | 0.15 | 1 | 0.15
|  | Single Phase Socket Outlet | 8 | 1000 | 0.85 | 9.4118 | 0.97 | 9.1294 | 0.5 | 4.5647
|  | Single Phase Socket Outlet 5 A | 5 | 1000 | 0.85 | 5.8824 | 0.8 | 4.7059 | 0.4 | 1.8824
| SDB 2-2 UPS | LED Round Emergency | 11 | 15 | 0.9 | 0.18333 | 1 | 0.18333 | 1 | 0.18333 | 1 | 8.4331 |  |  |  |  | 12.2219
|  | LED Round Emergency Wall | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333 | 1
|  | Single Phase Essential Socket | 18 | 1000 | 0.85 | 21.1765 | 0.97 | 20.5412 | 0.4 | 8.2165 | 0.97
290.5965