## Lux Calculation
LUX CALCULATION
FLOOR | S.N. | TYPES OF SPACE | AREA (mm^2) | REQUIRED LUX | BULB WATTAGE(W) | BULB EFFICIENCY | BULB LUMEN | µm | µu | N0. OF LUMINARIES
GROUND FLOOR PLAN | 1 | Foyer | 14.7 | 150 | 20 | 95 | 1900 | 0.8 | 0.8 | 1.8133
| 2 | Emergency Ward | 35.8 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 7.8509
| 3 | Drug and Instrument Store | 5.01 | 250 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.3734
| 4 | Nurse Station | 6 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.3158
| 5 | Staff Room | 7.1 | 150 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.1678
| 6 | Washing and Sorting | 25.71 | 150 | 15 | 95 | 1425 | 0.8 | 0.8 | 4.2286
| 7 | Packing/Ironing | 8.1 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.7763
| 8 | Store | 10.98 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.4079
| 9 | Sterilized Items Out | 8.8 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.9298
| 10 | Toilet(Male/Female) | 34 | 150 | 15 | 95 | 1425 | 0.8 | 0.8 | 5.5921
| 11 | Account Section | 10.21 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.239
| 12 | Registration | 10.34 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.2675
| 13 | OBS/Gynae Treatment | 12.15 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.6645
| 14 | Gynae Consultation | 9.7 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.1272
| 13 | Dental OPD | 18.7 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 4.1009
| 13 | Eye Clinic | 12.15 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.6645
| 13 | General Examination | 15.65 | 200 | 36 | 95 | 3420 | 0.8 | 0.8 | 1.43
| 15 | EPI/MCH/FP | 15.33 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 3.3618
| 16 | Pharmacy | 6.2 | 250 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.6996
| 17 | Pharmacy Store | 6.3 | 250 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.727
| 18 | Unnamed Room | 12.61 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.7654
| 19 | Corrider | 102.91 | 150 | 20 | 95 | 1900 | 0.8 | 0.8 | 12.6945
FIRST FLOOR PLAN | 20 | General Ward Male | 52.26 | 150 | 36 | 95 | 3420 | 0.8 | 0.8 | 3.5814
| 21 | Nurse Station+corrider | 58.2 | 150 | 15 | 95 | 1425 | 0.8 | 0.8 | 9.5724
| 22 | Dirty Utility | 9.4 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.0614
| 23 | Clean Utility | 9.4 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.0614
| 24 | Staff Room | 9.4 | 150 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.5461
| 25 | General Ward Female | 53.72 | 150 | 36 | 95 | 3420 | 0.8 | 0.8 | 3.6815
| 26 | Nurse Station+corrider | 44.42 | 150 | 15 | 95 | 1425 | 0.8 | 0.8 | 7.3059
| 27 | Labour Room | 14.72 | 250 | 15 | 95 | 1425 | 0.8 | 0.8 | 4.0351
| 28 | New Born Stebilisation | 10.5 | 250 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.8783
| 29 | Delivery Room | 26.21 | 250 | 36 | 95 | 3420 | 0.8 | 0.8 | 2.9936
| 30 | Sluice | 5.21 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.1425
| 31 | Clean Utility | 7.5 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.6447
| 43 | Corrider | 54.2 | 150 | 20 | 95 | 1900 | 0.8 | 0.8 | 6.6859
SECOND FLOOR PLAN | 32 | Doctor's Room | 12.81 | 200 | 36 | 95 | 3420 | 0.8 | 0.8 | 1.1705
| 33 | Pathology Lab | 13.7 | 300 | 15 | 95 | 1425 | 0.8 | 0.8 | 4.5066
| 34 | Meeting Room | 31.42 | 250 | 36 | 95 | 3420 | 0.8 | 0.8 | 3.5887
| 35 | EPI/MCH/FP | 13.38 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 2.9342
| 36 | Treatment Dressing | 13.5 | 250 | 15 | 95 | 1425 | 0.8 | 0.8 | 3.7007
| 37 | USG | 13.25 | 250 | 36 | 95 | 3420 | 0.8 | 0.8 | 1.5134
| 38 | ECG | 14.37 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 3.1513
| 39 | X-ray | 18.31 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 4.0154
| 40 | Blood Matching | 7.8 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.7105
| 41 | Blood Store | 7.2 | 200 | 15 | 95 | 1425 | 0.8 | 0.8 | 1.5789
| 42 | Major OT | 38.5 | 250 | 36 | 95 | 3420 | 0.8 | 0.8 | 4.3974
| 43 | Corrider | 56.15 | 150 | 20 | 95 | 1900 | 0.8 | 0.8 | 6.9264
|  |  | 172 | 150 | 20 | 95 | 1900 | 0.8 | 0.8 | 21.2171
|  |  | 35 | 150 | 20 | 95 | 1900 | 0.8 | 0.8 | 4.3174

## Load Calculation
HOSPITAL LOAD CALCULATION
| Hospital DBs | Electrical Loads |  |  |  | Apparent Power, kVA | Ku | Apparent Power Demand,kVA | Ks | Apparent Power Demand,kVA | Ks | Apparent Power Demand, kVA | Apparent Power Demand, kVA | Ks | Total Apparent Power Demand kVA | Size of Main MCCB of hospital, A | Total Size of sub MCCB, A | Size of Floor DBs MCCB,A
|  |  | Qty | Wattage, W | P.F
SDB 0 | SDB 0-1 | LED Panel Surface type 2x2 | 5 | 36 | 0.9 | 0.2 | 1 | 0.2 | 1 | 0.2 | 1 | 3.9443 | 58.6256 | 0.97 | 129.4768 | 187.6475 | 14.8468 | 84.9646
|  | LED Panel Surface type 1x4 | 4 | 40 | 0.9 | 0.17778 | 1 | 0.17778 | 1 | 0.17778
|  | LED Panel Surface type 1x1 | 12 | 15 | 0.9 | 0.2 | 1 | 0.2 | 1 | 0.2
|  | LED Panel Surface type 1x2 | 4 | 20 | 0.9 | 0.088889 | 1 | 0.088889 | 1 | 0.088889
|  | LED Panel Surface type 1x1 | 6 | 6 | 0.9 | 0.04 | 1 | 0.04 | 1 | 0.04 | [8 empty] | 28.9278
|  | Single Phase Socket Outlet 15 A | 2 | 1000 | 0.85 | 2.3529 | 0.97 | 2.2824 | 0.8 | 1.8259
|  | Single Phase Socket Outlet 5 A | 5 | 1000 | 0.85 | 5.8824 | 0.8 | 4.7059 | 0.3 | 1.4118
|  | Three Phase Socket Outlet | 1 | 9000 | 0.85 | 10.5882 | 0.85 | 9 | 0.7 | 6.3 | 1 | 6.3
|  | Electric Lift | 1 | 4000 | 0.8 | 5 | 0.9 | 4.5 | 1 | 4.5 | 1 | 4.5
| SDB 0-1 UPS | LED Round Emergency | 11 | 15 | 0.9 | 0.18333 | 1 | 0.18333 | 1 | 0.18333 | 1 | 6.9598 |  |  |  |  | 10.0867
|  | Single Phase Essential Socket | 16 | 1000 | 0.85 | 18.8235 | 0.9 | 16.9412 | 0.4 | 6.7765 | 1
| SDB 0-2 | LED Panel Surface type 2x2 | 4 | 36 | 0.9 | 0.16 | 1 | 0.16 | 1 | 0.16 | 1 | 7.3363 |  |  |  |  | 19.7627
|  | LED Panel Surface type 1x1 | 25 | 15 | 0.9 | 0.41667 | 1 | 0.41667 | 1 | 0.41667
|  | LED Panel Surface type 1x2 | 3 | 20 | 0.9 | 0.066667 | 1 | 0.066667 | 1 | 0.066667
|  | LED Panel Surface type 1x1 | 9 | 6 | 0.9 | 0.06 | 1 | 0.06 | 1 | 0.06
|  | Single Phase Socket Outlet | 12 | 1000 | 0.85 | 14.1176 | 0.97 | 13.6941 | 0.45 | 6.1624
|  | Single Phase Socket Outlet 5 A | 1 | 1000 | 0.85 | 1.1765 | 0.8 | 0.94118 | 0.5 | 0.47059 | [9 empty] | KVA of INVERTER
|  | Three Phase Socket Outlet | 1 | 9000 | 0.85 | 10.5882 | 0.85 | 9 | 0.7 | 6.3 | 1 | 6.3 | [7 empty] | 19.9602
| SDB 0-2 UPS | LED Round Emergency | 4 | 15 | 0.9 | 0.066667 | 1 | 0.066667 | 1 | 0.066667 |  | 5.5776 |  |  |  |  | 8.0835 |  |  | 19.2653
|  | LED Round Emergency Wall | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333 | [9 empty] | 8.4331
|  | Single Phase Essential Socket | 12 | 1000 | 0.85 | 14.1176 | 0.97 | 13.6941 | 0.4 | 5.4776 | 1
| SDB 0-3 | LED Panel Surface type 2x2 | 11 | 36 | 0.9 | 0.44 | 1 | 0.44 | 1 | 0.44 | 1 | 10.2848 |  |  |  |  | 14.9055
|  | LED Panel Surface type 1x1 | 7 | 15 | 0.9 | 0.11667 | 1 | 0.11667 | 1 | 0.11667
|  | LED Panel Surface type 1x2 | 19 | 20 | 0.9 | 0.42222 | 1 | 0.42222 | 1 | 0.42222
|  | LED Panel Surface type 1x1 | 15 | 6 | 0.9 | 0.1 | 1 | 0.1 | 1 | 0.1
|  | 48'' Celing Fan | 2 | 50 | 0.85 | 0.11765 | 0.85 | 0.1 | 1 | 0.1
|  | Single Phase Socket Outlet | 12 | 1000 | 0.85 | 14.1176 | 0.97 | 13.6941 | 0.5 | 6.8471
|  | Single Phase Socket Outlet 5 A | 8 | 1000 | 0.85 | 9.4118 | 0.8 | 7.5294 | 0.3 | 2.2588
| SDB 0-3 UPS | LED Round Emergency | 14 | 15 | 0.9 | 0.23333 | 1 | 0.23333 | 1 | 0.23333 | 1 | 7.4227 |  |  |  |  | 10.7576
|  | LED Round Emergency Wall | 3 | 15 | 0.9 | 0.05 | 1 | 0.05 | 1 | 0.05 | 1
|  | Single Phase Essential Socket | 18 | 1000 | 0.85 | 21.1765 | 0.97 | 20.5412 | 0.35 | 7.1894 | 1
SDB 1 | SDB 1-1 | LED Panel Surface type 2x2 | 10 | 36 | 0.9 | 0.4 | 1 | 0.4 | 1 | 0.4 | 1 | 8.2278 | 49.5456 |  |  |  | 11.9243 | 71.8052
|  | LED Panel Surface type 1x4 | 4 | 40 | 0.9 | 0.17778 | 1 | 0.17778 | 1 | 0.17778
|  | LED Panel Surface type 1x2 | 9 | 20 | 0.9 | 0.2 | 1 | 0.2 | 1 | 0.2
|  | LED Panel Surface type 1x1 | 6 | 6 | 0.9 | 0.04 | 1 | 0.04 | 1 | 0.04
|  | 48'' Celing Fan | 1 | 50 | 0.85 | 0.058824 | 0.85 | 0.05 | 1 | 0.05
|  | Single Phase Socket Outlet | 8 | 1000 | 0.85 | 9.4118 | 0.97 | 9.1294 | 0.6 | 5.4776 | [9 empty] | 47.6586
|  | Single Phase Socket Outlet 5 A | 5 | 1000 | 0.85 | 5.8824 | 0.8 | 4.7059 | 0.4 | 1.8824
| SDB 1-1 UPS | LED Round Emergency | 12 | 15 | 0.9 | 0.2 | 1 | 0.2 | 1 | 0.2 | 1 | 3.8518 |  |  |  |  | 5.5823
|  | Single Phase Essential Socket | 8 | 1000 | 0.85 | 9.4118 | 0.97 | 9.1294 | 0.4 | 3.6518 | 1
| SDB 1-2 | LED Panel Surface type 2x2 | 9 | 36 | 0.9 | 0.36 | 1 | 0.36 | 1 | 0.36 | 1 | 6.2986 |  |  |  |  | 29.3218
|  | LED Panel Surface type 1x4 | 6 | 40 | 0.9 | 0.26667 | 1 | 0.26667 | 1 | 0.26667
|  | LED Panel Surface type 1x1 | 17 | 15 | 0.9 | 0.28333 | 1 | 0.28333 | 1 | 0.28333
|  | LED Panel Surface type 1x2 | 6 | 20 | 0.9 | 0.13333 | 1 | 0.13333 | 1 | 0.13333
|  | LED Panel Surface type 1x1 | 3 | 6 | 0.9 | 0.02 | 1 | 0.02 | 1 | 0.02
|  | 48'' Celing Fan | 2 | 50 | 0.85 | 0.11765 | 0.85 | 0.1 | 1 | 0.1
|  | Single Phase Socket Outlet | 9 | 1000 | 0.85 | 10.5882 | 0.97 | 10.2706 | 0.5 | 5.1353
|  | Three Phase Socket Outlet | 1 | 9000 | 0.85 | 10.5882 | 0.97 | 10.2706 | 0.7 | 7.1894 | 1 | 7.1894
| SDB 1-2 UPS | LED Round Emergency | 8 | 15 | 0.9 | 0.13333 | 1 | 0.13333 | 1 | 0.13333 | 1 | 6.9804 |  |  |  |  | 10.0867
|  | Single Phase Essential Socket | 15 | 1000 | 0.85 | 17.6471 | 0.97 | 17.1176 | 0.4 | 6.8471 | 1
| SDB 1-3 | LED Panel Surface type 2x2 | 12 | 36 | 0.9 | 0.48 | 1 | 0.48 | 1 | 0.48 | 1 | 8.5644 |  |  |  |  | 12.4122 |  | 27.8909
|  | LED Panel Surface type 1x4 | 6 | 40 | 0.9 | 0.26667 | 1 | 0.26667 | 1 | 0.26667
|  | LED Panel Surface type 1x1 | 7 | 15 | 0.9 | 0.11667 | 1 | 0.11667 | 1 | 0.11667
|  | LED Panel Surface type 1x2 | 5 | 20 | 0.9 | 0.11111 | 1 | 0.11111 | 1 | 0.11111
|  | LED Panel Surface type 1x1 | 12 | 6 | 0.9 | 0.08 | 1 | 0.08 | 1 | 0.08
|  | 48'' Celing Fan | 3 | 50 | 0.85 | 0.17647 | 0.85 | 0.15 | 1 | 0.15
|  | Single Phase Socket Outlet | 8 | 1000 | 0.85 | 9.4118 | 0.97 | 9.1294 | 0.6 | 5.4776
|  | Single Phase Socket Outlet 5 A | 5 | 1000 | 0.85 | 5.8824 | 0.8 | 4.7059 | 0.4 | 1.8824
| SDB 1-3 UPS | LED Round Emergency | 11 | 15 | 0.9 | 0.18333 | 1 | 0.18333 | 1 | 0.18333 | 1 | 8.4331 |  |  |  |  | 12.2219
|  | LED Round Emergency Wall | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333 | 1
|  | Single Phase Essential Socket | 18 | 1000 | 0.85 | 21.1765 | 0.97 | 20.5412 | 0.4 | 8.2165 | 1
SDB 2 | SDB 2-1 | LED Panel Surface type 1x1 | 25 | 15 | 0.9 | 0.41667 | 1 | 0.41667 | 1 | 0.41667 | 1 | 9.0088 | 25.3101 |  |  |  | 13.0563 | 36.6813
|  | LED Round Emergency | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333
|  | Single Phase Socket Outlet | 15 | 1000 | 0.85 | 17.6471 | 0.97 | 17.1176 | 0.5 | 8.5588
| SDB 2-2 | LED Panel Surface type 2x2 | 12 | 36 | 0.9 | 0.48 | 1 | 0.48 | 1 | 0.48 | 1 | 7.8682 |  |  |  |  | 11.4031
|  | LED Panel Surface type 1x4 | 6 | 40 | 0.9 | 0.26667 | 1 | 0.26667 | 1 | 0.26667
|  | LED Panel Surface type 1x1 | 7 | 15 | 0.9 | 0.11667 | 1 | 0.11667 | 1 | 0.11667
|  | LED Panel Surface type 1x2 | 5 | 20 | 0.9 | 0.11111 | 1 | 0.11111 | 1 | 0.11111
|  | LED Panel Surface type 1x1 | 12 | 6 | 0.9 | 0.08 | 1 | 0.08 | 1 | 0.08
|  | LED Round Emergency | 11 | 15 | 0.9 | 0.18333 | 1 | 0.18333 | 1 | 0.18333
|  | LED Round Emergency Wall | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333
|  | 48'' Celing Fan | 3 | 50 | 0.85 | 0.17647 | 0.85 | 0.15 | 1 | 0.15
|  | Single Phase Socket Outlet | 8 | 1000 | 0.85 | 9.4118 | 0.97 | 9.1294 | 0.5 | 4.5647
|  | Single Phase Socket Outlet 5 A | 5 | 1000 | 0.85 | 5.8824 | 0.8 | 4.7059 | 0.4 | 1.8824
| SDB 2-2 UPS | LED Round Emergency | 11 | 15 | 0.9 | 0.18333 | 1 | 0.18333 | 1 | 0.18333 | 1 | 8.4331 |  |  |  |  | 12.2219
|  | LED Round Emergency Wall | 2 | 15 | 0.9 | 0.033333 | 1 | 0.033333 | 1 | 0.033333 | 1
|  | Single Phase Essential Socket | 18 | 1000 | 0.85 | 21.1765 | 0.97 | 20.5412 | 0.4 | 8.2165 | 0.97
290.5965