## Lux Calculation
LUX CALCULATION
FLOOR | S.N. | TYPES OF SPACE | LENGTH (m) | BREADTH (m) | AREA (m2) | REQUIRED LUX | TYPES OF LUMINARIES | BULB LUMEN | BULB WATTAGE | µm | µu | N0. OF LUMINARIES
GROUND | 1 | Foyer | 11.77 | 6.04 | 64 | 150 | LCTLRN-40-CDL(1X4) | 3800 | 40 | 0.8 | 0.8 | 3.9474 | https://www.alibaba.com/product-detail/LED-cloud-panel-40W-48W-ultra_62451658295.html?spm=a2700.7724857.main07.87.73461bff62ZJqC&fbclid=IwAR0w3RdNkR-FvGRpIRP5zyfwPlYpio3ILWOMOMwE_XWn_tJuOk3RTx3scoE
| 2 | Register | 5.975 | 6.04 | 14.7 | 200 | LHEWEJP6PW1W020 | 2000 | 20 | 0.8 | 0.8 | 2.2969
| 3 | Restroom 1 | 10.77 | 6.04 | 11.7 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 3.0469
| 4 | Restroom 2 | 5.75 | 5.9 | 11 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 2.8646
| 5 | Utility |  |  | 5.86 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 1.526
| 6 | OPD |  |  | 18.6 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.875
| 7 | Toilet |  |  | 11.5 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 2.9948 | LHECDIL7PP1W036 | INR 3255
| 8 | Pedriatric Play Room |  |  | 25 | 150 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.9062
| 9 | Pedriatric OPD | 28.64 | 12.04 | 16.75 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.4896
| 10 | Gynae OPD | 5.077 | 4.017 | 49.6 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 10.3333
| 11 | OPD 7 | 5.75 | 5.9 | 18.9 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.9375
| 12 | Toilet |  |  | 5.2 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 1.3542
| 13 | Janitor | 9.11 | 5.77 | 2.27 | 150 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 0.88672
| 14 | OPD 6 | 9.11 | 6.04 | 12.86 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.6792
| 15 | Reception | 6.54 | 6.04 | 7.68 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.6
| 16 | OPD 5 | 6.54 | 5.77 | 13.8 | 250 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.5938
| 17 | Female Toilet | 8.3 | 5.77 | 23.4 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 6.0938
| 18 | Wheel Chair W/C | 8.3 | 6.04 | 3.3 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 0.85938
| 19 | Male Toilet | 5.77 | 4.17 | 23.4 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 6.0938
| 20 | Reception | 5.75 | 5.9 | 8.16 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.7
| 21 | OPD 1 |  |  | 11.98 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.4958
| 22 | OPD 2 | 6.985 | 4.145 | 12.38 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.5792
| 23 | OPD 3 | 5.475 | 4.145 | 12.36 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.575
| 24 | OPD 4 | 11.145 | 6.04 | 12.49 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.6021
| 25 | CT-Scan | 3.77 | 6.02 | 33.15 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 6.9062
| 26 | Operator Room |  |  | 9.6 | 150 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 3.75
| 27 | Report Dispatch | 11.725 | 4 | 9.66 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.0125
| 28 | Radiologist |  |  | 7.78 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.6208
| 28 | ECHO/ECG | 39 | 10 | 12.4 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.5833
| 29 | Holter |  |  | 16.47 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.4312
| 30 | USG | 18 | 6 | 12.3 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.5625
| 31 | UPS Technical |  |  | 8.4 | 150 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 3.2812
| 32 | X - Ray | 9 | 6 | 20 | 150 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 7.8125
| 33 | Dark Room | 8.75 | 3.625 | 4.2 |  | LCDE-09-CDL | #REF! | 9 | 0.8 | 0.8 | #REF!
| 34 | OPD 13 | 13.27 | 2.25 | 12.01 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.5021
| 35 | OPD 14 | 16.5 | 5.4 | 12.05 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.5104
| 36 | OPD 15 |  |  | 12 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.5
| 37 | Electrical Room | 94 | 59 | 5.8 | 150 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 0.90625
| 38 | Enquiry |  |  | 12.4 | 150 | LCTLRN-40-CDL(1X4) | 3800 | 40 | 0.8 | 0.8 | 0.7648
| 39 | Physiotherapy |  |  | 12.86 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.6792
| 40 | Immunization |  |  | 12.86 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.6792
| 41 | Pharmacy |  |  | 30 | 300 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 3.9062
| 42 | Philebotomy |  |  | 6.2 | 300 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.9375
| 43 | Report Sample |  |  | 10.5 | 250 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.7344
| 44 | Chief Pathologist |  |  | 8.5 | 300 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.6562
| 45 | Hematology |  |  | 8.5 | 300 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.6562
| 46 | Histo-pathology |  |  | 8.5 | 300 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.6562
| 47 | Bio chemistry |  |  | 35.94 | 300 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 4.6797
| 48 | Serology |  |  | 6.336 | 300 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.98
| 49 | Virology |  |  | 6.33 | 300 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.9781
| 50 | Micro Biology |  |  | 13.09 | 300 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 1.7044
| 51 | Intake and Sort |  |  | 10.9 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.2708
| 52 | Issue |  |  | 10.9 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.2708
| 53 | Wash |  |  | 13.4 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.7917
| 54 | Store |  |  | 16.6 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.4583
| 55 | Sterlize |  |  | 13.12 | 300 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 4.1
| 57 | Drying/Pack |  |  | 18 | 250 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 4.6875
| 58 | Restroom |  |  | 20.6 | 200 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 1.7882
| 59 | Sluice |  |  | 9 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.875
| 60 | Blood Bank |  |  | 19.4 | 300 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 2.526
| 61 | X-Ray |  |  | 19 | 150 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 7.4219
| 62 | Doctors OPD |  |  | 19.13 | 200 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 1.6606
| 63 | Paramedics |  |  | 15.66 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.2625
| 64 | Paramedics Restroom |  |  | 19 | 100 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.9792
| 65 | Police Room |  |  | 19 | 150 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.9688
| 66 | Medical Legal Case |  |  | 19 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.9583
| 67 | Emergency Ward |  |  | 70.8 | 200 | LHEWEIP7PW1W030(4x1) | 3000 | 30 | 0.8 | 0.8 | 7.375
| 68 | Isolation |  |  | 6.8 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.4167
| 69 | Mini ICU |  |  | 49.5 | 200 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 4.2969
| 70 | Minor OT |  |  | 49.6 | 200 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 4.3056
| 71 | Duty Doctor Room |  |  | 12.4 | 300 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 1.6146
| 72 | Pantry |  |  | 7.4 | 150 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.1562
| 73 | Nurse Restroom |  |  | 12.5 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.6042
| 74 | Dressing /Plaster |  |  | 49.64 | 300 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 6.4635
| 75 | Dots Clinic |  |  | 11.23 | 250 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.9245
| 76 | OPD Entrance Corrider |  |  | 78.2 | 150 | LHEWEJP6PW1W020 | 2000 | 20 | 0.8 | 0.8 | 9.1641
| 77 | Courtyard Corrider |  |  | 141.56 | 150 | LHEWEJP6PW1W020 | 2000 | 20 | 0.8 | 0.8 | 16.5891
| 78 | Emergency Corrider |  |  | 48.36 | 150 | LHEWEJP6PW1W020 | 2000 | 20 | 0.8 | 0.8 | 5.6672
FRIST | 79 | Delivery Room |  |  | 25.7 | 250 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 6.6927
| 80 | Baby Bathing+Breast Feeding |  |  | 32 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 6.6667
| 81 | Checking Room + Doctor Room |  |  | 18.26 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.8042
| 82 | Janitor |  |  | 4.12 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 1.0729
| 83 | Gynae Ward |  |  | 61.89 | 200 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 5.3724
| 84 | Pediatric Ward |  |  | 62.5 | 200 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 5.4253
| 85 | Male Medical Ward |  |  | 27.66 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 5.7625
| 86 | Female Medical Ward |  |  | 25.35 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 5.2812
| 87 | Cabin 1 |  |  | 14.3 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.9792
| 88 | Cabin 2 |  |  | 22.06 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 4.5958
| 89 | Post Operative Ward |  |  | 56.3 | 150 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 8.7969
| 90 | Change Room |  |  | 6.3 | 100 | LSDE-06-CDL | 600 | 6 | 0.8 | 0.8 | 1.6406
| 91 | Duty Station |  |  | 12.6 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.625
| 92 | Orthopedic Ward |  |  | 17.1 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.5625
| 93 | Female Surgery Ward |  |  | 36.1 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.5208
| 94 | Male Surgery Ward |  |  | 31.92 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 6.65
| 95 | Treatment Room |  |  | 8.95 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.8646
| 96 | Nurse Duty Station |  |  | 6.8 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.4167
| 97 | Nurse Restroom |  |  | 10.49 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.1854
| 98 | NICU * |  |  | 35 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.2917
| 99 | PICU * |  |  | 34.5 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.1875
| 100 | ICU * |  |  | 78.8 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 16.4167
| 101 | OT 1 ** |  |  | 32.3 | 200 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 2.8038
| 102 | OT 2 ** |  |  | 34.73 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.2354
| 103 | OT 3 ** |  |  | 35 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.2917
| 104 | Recovery |  |  | 33 | 200 | LHEWEJP6PW1W020 | 2000 | 20 | 0.8 | 0.8 | 5.1562
| 105 | Anesthesia |  |  | 8 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.6667
| 106 | Sterile Corridor |  |  | 44.2 | 200 | LHEWEJP6PW1W020 | 2000 | 20 | 0.8 | 0.8 | 6.9062
| 107 | Sterile Store |  |  | 8.2 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.7083
| 108 | Medical Store |  |  | 8 | 300 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.5
| 109 | OT Doctor Restroom |  |  | 36.6 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.625
| 110 | Ward Doctor Rest room |  |  | 13.8 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 2.875
| 111 | Nurse Restroom |  |  | 15.1 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.1458
| 112 | Red Zone |  |  | 26.6 | 200 | LHEWEJP6PW1W020 | 2000 | 20 | 0.8 | 0.8 | 4.1562
| 113 | OT Reception |  |  | 8.5 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.7708
| 114 | Nurse Station and Periphery |  |  | 65.24 | 200 | LHEWEJP6PW1W020 | 2000 | 20 | 0.8 | 0.8 | 10.1937
TOP | 115 | Library |  |  | 58.4 | 350 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 8.8715
| 116 | IT Room |  |  | 19.8 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 4.125
| 117 | General Ward 1,2 |  |  | 60 | 200 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 5.2083
| 118 | Nurse Duty Station |  |  | 17.9 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 3.7292
| 119 | General Ward 3 |  |  | 34.1 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.1042
| 120 | General Ward 4 |  |  | 41.5 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 8.6458
| 121 | Account |  |  | 25.33 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 5.2771
| 122 | Administration |  |  | 28.6 | 250 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.4479
| 123 | Auditorium Hall |  |  | 50.4 | 300 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 6.5625
| 124 | Meeting Hall |  |  | 33.7 | 300 | LHECDIL7PP1W036 (2x2) | 3600 | 36 | 0.8 | 0.8 | 4.388
| 125 | Director office |  |  | 27.5 | 250 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 7.1615
| 126 | Deputy Director Office |  |  | 18.7 | 250 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 4.8698
| 127 | Waiting Space |  |  | 25.6 | 150 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 4
| 128 | Reception |  |  | 8.2 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.7083
| 129 | Store |  |  | 5.7 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.1875
| 130 | Pantry |  |  | 8.8 | 150 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 1.375
| 131 | Staff Canteen |  |  | 45 | 200 | LHEWEJP6PW1W015 | 1500 | 15 | 0.8 | 0.8 | 9.375

## Load Calculation
MAIN EXHIBITION HALL
Electrical Loads |  |  |  |  | Apparent Power, kVA | Factor of Max. Utilization | Apparent Power Demand,kVA | Diversity Factor | Apparent Power Demand,kVA | Diversity Factor | Apparent Power Demand, kVA | Total Apparent Power Demand, kVA | Size of Main MCCB, A | Size of DBs MCCB,A
|  | Qty | Wattage, W | P.F
Light and Fan | LED Round Recess | 723 | 20 | 0.9 | 16.0667 | 1 | 16.0667 | 1 | 16.0667 | 1 | 22.9236 | 170.381 | 246.9289 | 34.7327
| LED Suspended Tube light | 135 | 36 | 0.9 | 5.4 | 1 | 5.4 | 1 | 5.4
| Décor Light | 8 | 20 | 0.9 | 0.17778 | 1 | 0.17778 | 1 | 0.17778
| High Beam Light | 8 | 50 | 0.9 | 0.44444 | 1 | 0.44444 | 1 | 0.44444
| Spot Light | 10 | 12 | 0.9 | 0.13333 | 1 | 0.13333 | 1 | 0.13333
| Exhaust Fan | 27 | 30 | 0.8 | 1.0125 | 1 | 1.0125 | 1 | 1.0125
Power Socket | Single Phase Socket Outlet | 231 | 1000 | 0.95 | 243.1579 | 0.97 | 235.8632 | 0.6 | 141.5179 | 0.97 | 147.4574 |  |  | 223.4202
| Three Phase Socket Outlet | 5 | 3000 | 0.95 | 15.7895 | 0.95 | 15 | 0.7 | 10.5
Current Rating -light,1 ph and 3 ph resp.
DB 1 | LED Round Recess | 199 | 20 | 0.9 | 4.4222 | 1 | 4.4222 | 1 | 4.4222 | 1 | 9.0142 | 167.3843 | 242.5859 | 68.9664 | 13.6578
| LED Suspended Tube light | 99 | 36 | 0.9 | 3.96 | 1 | 3.96 | 1 | 3.96
| Décor Light | 4 | 20 | 0.9 | 0.088889 | 1 | 0.088889 | 1 | 0.088889
| High Beam Light | 8 | 50 | 0.9 | 0.44444 | 1 | 0.44444 | 1 | 0.44444
| Spot Light | 10 | 12 | 0.9 | 0.13333 | 1 | 0.13333 | 1 | 0.13333
| Exhaust Fan | 5 | 30 | 0.8 | 0.1875 | 1 | 0.1875 | 1 | 0.1875
| Single Phase Socket Outlet | 60 | 1000 | 0.95 | 63.1579 | 0.97 | 61.2632 | 0.58 | 35.5326 | 0.97 | 36.5037 |  |  |  | 53.8373
| Three Phase Socket Outlet | 1 | 3000 | 0.95 | 3.1579 | 0.95 | 3 | 0.7 | 2.1 | [5 empty] | 3.1818
DB 2 | LED Round Recess | 251 | 20 | 0.9 | 5.5778 | 1 | 5.5778 | 1 | 5.5778 | 1 | 6.2453 |  |  | 69.123 | 9.4625
| LED Suspended Tube light | 12 | 36 | 0.9 | 0.48 | 1 | 0.48 | 1 | 0.48
| Décor Light | 4 | 20 | 0.9 | 0.088889 | 1 | 0.088889 | 1 | 0.088889
| Exhaust Fan | 5 | 30 | 0.8 | 0.1875 | 1 | 0.1875 | 1 | 0.1875
| Single Phase Socket Outlet | 65 | 1000 | 0.95 | 68.4211 | 0.97 | 66.3684 | 0.58 | 38.4937 | 0.97 | 39.3759 |  |  |  | 58.3238
| Three Phase Socket Outlet | 1 | 3000 | 0.95 | 3.1579 | 0.95 | 3 | 0.7 | 2.1 | [5 empty] | 3.1818
DB 3 | LED Round Recess | 139 | 20 | 0.9 | 3.0889 | 1 | 3.0889 | 1 | 3.0889 | 1 | 3.8689 |  |  | 60.6553 | 5.862
| LED Suspended Tube light | 12 | 36 | 0.9 | 0.48 | 1 | 0.48 | 1 | 0.48
| Exhaust Fan | 8 | 30 | 0.8 | 0.3 | 1 | 0.3 | 1 | 0.3
| Single Phase Socket Outlet | 54 | 1000 | 0.95 | 56.8421 | 0.97 | 55.1368 | 0.6 | 33.0821 | 0.97 | 36.1636 |  |  |  | 50.1244
| Three Phase Socket Outlet | 2 | 3000 | 0.95 | 6.3158 | 0.95 | 6 | 0.7 | 4.2 | [5 empty] | 6.3636
DB 4 | LED Round Recess | 139 | 20 | 0.9 | 3.0889 | 1 | 3.0889 | 1 | 3.0889 | 1 | 3.8689 |  |  | 54.8678 | 5.862
| LED Suspended Tube light | 12 | 36 | 0.9 | 0.48 | 1 | 0.48 | 1 | 0.48
| Exhaust Fan | 8 | 30 | 0.8 | 0.3 | 1 | 0.3 | 1 | 0.3
| Single Phase Socket Outlet | 51 | 1000 | 0.95 | 53.6842 | 0.97 | 52.0737 | 0.6 | 31.2442 | 0.97 | 32.3439 |  |  |  | 47.3397
| Three Phase Socket Outlet | 1 | 3000 | 0.95 | 3.1579 | 0.95 | 3 | 0.7 | 2.1 | [5 empty] | 3.1818